Anglo Coal (Dawson Management) Pty Ltd

ABN 15 006 746 701

Dawson Highway, Moura, 4718.

Ph:   (07) 4990 9902

Fax: (07) 4990 9800

All correspondence to:

PO Box 225, Moura, QLD, 4718.

Specification

For

Commissioning of Electrical

Installations and

Electrical Equipment

At

Dawson Mine

# SAFETY

Commissioning of electrical equipment often involves working with live electrical equipment and conductors exposed.  Everyone’s “Duty of Care” requires that all procedures and activities are conducted in accordance with the requirements of:-

- Queensland Coal Mining Safety and Health Act 1999;

- Queensland Coal Mining Safety and Health Regulations 2001;

- Queensland Electricity Act and Regulations;

- Moura Coal Mining Site procedures;

- Industry best practice; and

- Specific procedures developed at the time for a specific task.

The objective is to prevent any person being exposed to any unacceptable risk.

# PURPOSE

This specification describes the process whereby an installation is checked and tested from construction to load commissioning and records these activities.  The specification also provides inspection and testing activities.

These test sheets shall be used for all modifications and installations, unless alternative sheets are approved by the Company’s electrical engineering manager (‘EEM’).

# SCOPE

The procedure consists of three steps or phases.

## Pre-Commissioning, Inspecting and Testing

During this phase all inspections and tests are carried out to prove that equipment has been supplied and installed as specified and is in a fit state to be energised.  This phase includes, but is not limited to, inspections and tests involving:

- continuity;

- insulation;

- phasing;

- polarity;

- ratios;

- calibrations;

- adjustments;

- protective devices; and

- relay setting.

- Ductor testing

## No-load Commissioning, Inspecting and Testing

During this phase all inspections and tests are carried out to prove that the equipment performs as designed under “no-load” conditions.  This phase includes:

- initial energisation;

- testing of controls;

- instrumentation; and

- the logical operation of sequenced systems.

## Load Commissioning, Inspecting and Testing

During this phase all inspections and tests are carried out to prove that equipment performs as designed under “full-load” conditions.  This phase includes

- the recording of load currents;

- logical sequence operations; and

- restarts underload to prove equipment operates as designed.

N.B.  The inspection and testing report sheets will overlap areas.

# REFERENCES

- Queensland Coal Mining Safety and Health Act 1999;

- Queensland Coal Mining Safety and Health Regulations 2001;

- AS 3000:2000;

- AS 3007;

- AS 1026;

- AS 1136;

- AS 1429;

- AS 1747;

- AS 1981;

- AS 2067; and

- AS 2191.

# SPECIFIC REQUIREMENTS

## INTRODUCTION

    - The Contractor shall be responsible for the execution of all inspections, testing and commissioning of the electrical systems associated with the Project Specification as detailed in this section of this Specification and as deemed necessary by the Company Representative.

    - The Contractor shall record results of all tests on the reports as provided in this Specification or as approved by the EEM.

    - Arrangements will be made by the Company Representative for all test results to be stored electronically.

    - A copy of each of the Electrical Inspection/Test Report forms available for use by the Contractor is included in Appendix No.1.

    - One of the Contractors Personnel shall be nominated to be responsible to the Company Representative for the overall testing and commissioning of the electrical systems as required under this section.

    - The Contractor Representative shall hold qualifications acceptable to the Company Representative and evidence of these qualifications must be submitted to upon request to the Company Representative prior to the commencement of the testing and commissioning functions.

    - All commissioning and testing is to be conducted in the presence of the Company Representative or Delegate.  To this end, the Contractor shall notify the Company Representative in writing 48 hours prior to the proposed commencement of any checks, inspections or tests.

    - Should any dispute whatsoever arise from results so recorded, the Company Representative may direct the Contractor to repeat the tests in whole or in part at the Contractors expense.

    - All electrical equipment shall be subject to, and withstand satisfactorily, such type tests as are specified in the appropriate Australian Standard Specification where the manufacturer is unable to produce evidence of satisfactory compliance by identical equipment with these type tests.

    - The Contractor shall be responsible for the proper testing of work completed, or plant or materials supplied by the Contractors Sub Contractor, to the same extent as if the work, plant or material were completed or supplied by the Contractor.

    - If faults are found in materials or equipment furnished by others, which are due to improper or incorrect manufacturing, fabrication or shipping of the materials or equipment, the Contractor shall notify the Company Representative in writing.  The Company Representative will issue instructions for the method of handling the necessary corrections or replacements.

## TEST INSTRUMENTS

    - The Contractor shall provide all test equipment with current calibration certificate to enable proper testing and commissioning of all electrical equipment installed by the Contractor and the Contractors Sub Contractors.  The test date of the equipment check must be on the test instrument.

## PRE-COMMISSIONING, INSPECTIONS AND TESTING

    - The objective of pre-commissioning inspections, checks and tests is to ensure that the whole of the work associated with the electrical system(s) covered by the Project Specification has been completed both mechanically and electrically and that all identification plates, labels and ferrules have been fitted and that the installation is ready to be tested and then commissioned.

    - The following elementary inspections, checks and tests shall be carried out by the Contractor at this stage:

- before making the equipment live, carry out a visual inspection of all electrical apparatus and associated equipment, checking that all items of electrical equipment and their mechanical supports have been securely mounted, are plumb and that no corrosion of metal parts is evident;

- tests shall be made on all lines and circuits after erection to establish insulation resistance and absence of accidental earth connections;

- check that all supply sources are active and at the correct voltage;

- check that all hinges and operators are free and have been lubricated;

- check that all pieces of electrical equipment are free to operate, free from oxidation and correctly rated for their duty;

- carry out a through visual check of all earth connections, electrodes and associated cabling, with particular attention being paid to ensure that clamps, joints and points of termination have been properly executed and that each system is electrically and mechanically continuous;

- using a continuity tester, carry out a point to point check of the internal wiring of all motor starters, distribution equipment and control devices to determine that the wiring is correct to the information supplied to be Contractor and that each conductor is terminated to the correct terminal; These point to point checks are to be extended to any wiring whose connections may have been altered, disconnected or swapped.

- check that all wiring is correctly ferruled and that ferrules are correctly aligned on each wire;

- all High-Current connections shall be ductor tested to confirm there are no high resistance joints.

- ensure that all equipment located in defined hazardous areas has been properly installed and is correctly classified and certified for use therein.  Particular attention shall be paid to ensure that enclosures are sound, free from mechanical damage and complete with all screws and bolts;

- check that all enclosures are free of extraneous matter and wire clippings, and are left clean;

- check that cables have been fitted with all the required identification tags and that the tags are secure and bear the correct identification reference;

- inspect all pipes, conduits, trays, racks, brackets and fixings to ensure that they are correctly fixed and located, are free from corrosion and adequately sized for their duty;

- check tension on all bolts including load side bolts, line side bolts and any bolts securing busbar/cables leading away from this cabinet. Mark which bolts have been tensioned.

- ensure that all covers, lids and plates are fitted and that all screws are in place;

- check that all luminaries have been correctly wired and mounted, are free from corrosion, are complete with all screws and are fitted with the correct type and size of lamp or tube;

- check that all power outlets are correctly fitted and wired; and

- covers of all equipment shall be removed by the Contractor to allow inspection of workmanship and all shall be replace, after clearance by the Company Representative, by the Contractor.

## OPERATIONAL TESTING AND COMMISSIONING

### General

      - The Contractor shall, under the supervision of the Company Representative or Delegate, commission all items of plant and equipment, and carry out any adjustments to electrical equipment required.

      - The Contractor shall be responsible for the carrying out of all tests as instructed by the Company Representative (SOP 0087 shall be followed).  These tests shall include, but are not necessarily limited to the following:

- function test all electrical systems and circuits and make any necessary adjustments;

- adjust all control and protective devices and their operating mechanisms to ensure their correct operation, as directed by the Company Representative;

- record results of tests carried out on the appropriate test sheets as indicated below;

- make a final check that all enclosures, covers and doors are secured and all padlocks fitted as applicable; and

- at the conclusion of test and as directed by the Company Representative, remove all warning signs and hand over all keys.

### Tests at Manufacturer’s Works and at Site

      - The Company Representative or Delegate, shall witness all tests.

      - The testing of switchgear and control gear assemblies witnessed may include but not necessarily be limited to the following:

- routine tests as outlined in AS 1136 for voltages up to 1000V;

- routine tests as outlined in AS 2067 for voltages above 1000V.

- 50% trip volt test;

- 80% hold in contractor test;

- primary and secondary injection tests; and

- all switches tested for active switching.

      - Test sheets of type tests shall be made available to the Company Representative.

      - Not less than seven days written notice shall be given prior to tests for witnessing by the Company or their Delegate.

### Tests of Power and Control Cables up to 0.6/1kV (Test Sheet ET 1)

      - All cables shall be subjected to insulation tests of 1000V phases to phase and 500V phases to neutral, phase to earth and neutral to earth.  The minimum acceptable reading shall be as per AS/NZS 3000:2000.

### Tests of 3.3kV, 11kV and 22kV Cables (Test Sheet ET2)

      - All cables shall be subject to insulation tests of 5000V phase to earth and phase to phase before and after a high voltage test.  The insulation tests after the high voltage test should not be significantly less than the insulation test before.

      - All new installed cables shall be subject to a DC voltage test as set out in the relevant Australian Standard, either AS1026 or AS1429 Part 1.  Cores not under test are to be earthed during this test.

      - Cables previously in service or connected to equipment shall be subjected to a reduced voltage test, as directed by the Company Representative.

      - Before termination of any cable, a full phasing check shall be carried out.  A record of phasing and termination details of all inline joints is to be supplied by the Contractor.

      - All new trailing cables shall be supplied with a certificate recording testing as required by AS 1747.

### Tests of Earthing Systems (Test Sheet ET 3)

      - With the use of the ground testing meter, determine the earth grid resistances as specified on earthing drawings.  If necessary, add earth rods and earthing conductor until the required earthing value has been attained.

      - Check all earthing test bars and connections.

      - Check, if required, that HV and LV earthing systems are effectively separated.

      - After completion of individual earth tests, the overall earthing resistance will be measured.  Resistance values shall not exceed 1 ohm for electrical earth systems or 10 ohms for static or lightning earth systems.

### Tests of Transformers (Test Sheet ET 4)

      - Check that transit packing is removed from explosion vent and breather.

      - Check, tighten all bolts and ensure that there are no oil leaks, check all bushings for cracks and chips.

      - Take oil samples from the bottom of the transformer tank and from each drum being used for topping up and test as detailed in Clause 5.4.9.  Check oil levels, after checking that all oil valves are fully opened.  Check that silica gel in the breather is deep blue in colour.

      - With sealed transformer, check that nitrogen pressure is maintained at correct value and oil level is correct.

      - Check that auxiliary equipment is set and operates at correct values, i.e. buccholz, temperature and pressure alarms.

      - Check temperature and resistance of each winding.

      - Check insulation resistance of each winding.  NOTE: a high voltage test may be required as directed by the Company Representative if there are indications of transit damage.

      - Check tap changes for correct movement.  Select each tap in turn and measure voltage.

      - Check name plate data against transformer data sheets.

        - Check phasing of primary and secondary circuits to ensure continuity of phase connections across transformer.

### Tests of Distribution Equipment (Test Sheets ET 5 and ET 6)

      - Carry out routine tests as outlined in AS 1136, voltages up to 1000V.

      - Test load balances over phases.  More than 20% out of balance will not be acceptable.  All work necessary to achieve an acceptable balance of load shall be at the Contractor’s expense.

      - Carry out routine tests as outlined in AS2067, for voltages above 1000V.

      - Take oil samples and test as detailed in Clause 5.4.9.

      - Check direction of rotation of kilowatt-hour meter.

### Tests of Motor Control Centres (Test Sheets ET 6 and ET 12)

      - Carry out routine tests as outlined in AS 1136, for voltages up to 1000V.

      - Carry out routine tests as outlined in AS 2067, for voltages above 1000V.

      - Test operating time of overload relays at three times full load current.  Set overload relays at 100% full load current of motor.

      - Test earth leakage protection relays.

      - Set control equipment as directed by the Company Representative.

### Test of Insulating Oil (Test Sheet ET 7)

      - New insulating oil for switchgear and transformers shall be tested for dielectric strength as outlined in AS1767.  If oil has been supplied in more than one container, then each container shall be tested.  Should the oil be transferred into a bulk container, three samples from the bulk container shall be tested.  The Contractor shall adhere to the requirements laid down in AS1767 governing the handling and testing of insulating oils.

      - Samples of oil shall be tested for the presence of excessive moisture by a crackle test as set out in AS1767 sub notes to Table 1.  If two out of three tests fail, the oil should not be used.

      - Before filling oil tanks, the Contractor shall carefully clean and inspect them and ensure that the correct level of oil is provided.

### Test of Conveyors (Test Sheet ET 8)

      - Check operation of all safety equipment installed on conveyor, i.e. pull wire switches, start warning siren and emergency stop buttons.

      - Test and set all control equipment, i.e. timing relays, belt drift switches, under speed switches, blocked chute relays, thermostat, limit switches and water sprays.

      - Check operation of brake and brake limit switch.

      - Adjust brake and check run on time of conveyors both unloaded and loaded.

      - Check and test operation of all alarms.

      - Check for belt slippage when started with full load.

### 5.4.11	Test of Protection Relays (Test Sheet ET 9)

      - Manually check operation of tripping mechanism, intertrips and moving element.

      - Check current transformer winding for polarity, ratio and continuity.

      - Carry out injection test.  NOTE: earth leakage tests shall be primary injection.  Other tests may be primary injection where practical.  Where not practical, secondary injection is acceptable if step 5.4.11.2 is completed.

      - Test auxiliary and trip voltage supplies.

      - Check operation of trip and alarm circuits.

### Tests of Electric Motors (Test Sheet ET 10 or ET 11)

      - Check insulation resistance using 5000V for high voltage motors, 1000V for low voltage motors and 500V for single-phase low voltage motors.  Where required, the insulation shall be dried out by a method approved by the Company Representative.

      - Check motor for rotation.  The Contractor must establish the true direction of rotation required.  Correct phasing and direction of rotation shall be the responsibility of the contractor and any damage arising from failure to do suck, shall be at the Contractor’s expense.  The full expense of replacing or repairing equipment damaged due to incorrect direction of rotation of motors shall be born by the Contractor.

      - Check bearings for brinelling.

      - Measure resistance of external resistor grids, set stage timers and measure stator current for each stage.

      - Check brush tension and that brushes are correctly seated.

      - Check operation of more anti-condensation heaters.

      - Check resistance of thermistor and operation of thermistor relay.

      - Check bearing temperature after a four-hour run at no load.

      - Check no load and normal load current and voltage.

### Test of Lighting (Test Sheet ET 13)

      - In outdoor locations, floodlights shall first be set to generally direct light into the specified areas and then having observed the general effect with the light switched on during darkness, final adjustment shall be made to the aiming angles of the luminaries to obtain as even a light distribution as possible in the specified areas.

      - The Company Representative shall take a series of illumination level tests in a regular pattern and the values obtained marked onto a plan of the area tested.

      - All measurements of illumination shall be in the horizontal plane and at the normal working level of the area or location under test.

      - A discharge test shall be carried out on all batter operated emergency light units to establish the capacity of the batteries.

### Test of Batteries (Test Sheet ET 21)

      - Tests shall be carried out in accordance with AS 1981 and AS 2191, depending on the type of batteries supplied and shall include a discharge test to establish the capacity of the batteries at the five hour discharge rate.

      - Batteries supplied dry shall be fitted and charged in accordance with the manufacturer’s instructions.  All batteries shall be tested and given an equalising charge before placing into operation.

      - The date of battery installation shall be painted on the side of the battery.

### Lighting and Small Power Circuits (Test Sheets ET 16, 17, 18)

      - All lighting and small power circuits shall be tested to satisfy the requirements of AS 3000 and in accordance with Handbooks “Service Polarity Testing” and “Testing Procedures for Customer’s Installations.

### High Voltage Powerlines and Switch Yards (Test Sheets ET 19, 20)

      - All High Voltage powerlines and switch yards shall be inspected for compliance with specifications during and after completion of construction and before testing and energisation.  Inspection detail should include, but not be limited to :

- span distances;

- sag of conductors;

- condition of Insulators;

- hardware correctly mounted;

- earth switches on correct side of isolation switches;

- connections correctly made and secure; and

- correct operation of all switches and interlocks.

      - All High Voltage powerlines and switch yards will have appropriate testing to prove integrity of insulation carried out prior to energisation.  The testing to be carried out will be nominated by Moura Coal Mining for the specific project and will include Megger and High Potential Testing to suit the project.  AS 2989 – Section 5 tests should be used as a guideline.

# APPENDIX: STANDARD TEST SHEETS

# ET 1	0.6/1.1 kV POWER CABLE INSPECTION AND TEST REPORT

| SUBSTATION: |  |  |  |  |  |  | CABLE No: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SWITCHYARD: |  |  |  |  |  |  | CABLE TYPE: |  |  |  |  |  |  | SIZE: |  |  |
| CABLE ROUTE: FROM: |  |  |  |  |  |  | TO: |  |  |  |  |  |  |  |  |  |
| Cable Installation Checks |  |  |  |  |  |  | Comments: |  |  |  |  |  |  |  |  |  |
| Correctly Routed: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Correctly Supported: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Correct Bend Radii: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| END | Correct ID Tags | Correct Gland & Fit |  |  | Correct Lugs & Fit |  |  |  | Correct Ferrules & Numbers |  |  | Correct Earthing |  |  |  | Correct Polarity |
| A END |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B END |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Instruments |  |  | Type |  |  | Serial No. |  |  |  | Voltage |  |  |  |  | Calibration Cert. No. |  |
|  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Conductor |  |  | Continuity |  |  |  |  | Insulation |  |  |  |  | Comments |  |  |  |
| Earth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Red to White |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Red to Blue |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| White to Blue |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Red to Earth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Blue to Earth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| White to Earth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Red to Neutral |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| White to Neutral |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Blue to Neutral |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Neutral to Earth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  | Tested By: Print Name: Sign: |  |  |  |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |  |  |  |  |  |

# ET 2	HIGH VOLTAGE CABLE INSPECTION AND TEST REPORT

| SUBSTATION: |  |  |  |  |  |  |  |  | CABLE No: |  |  |  |  |  |  | VOLTS: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SWITCHYARD: |  |  |  |  |  |  |  |  | CABLE TYPE: |  |  |  |  |  |  | SIZE: |  |  |  |
| CABLE ROUTE FROM: TO: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| END | Correct ID Tags |  | Correct Kit & Fit |  |  | Correct Lugs & Fit |  |  |  |  | Correct Numbering |  |  |  | Correct Earthing |  |  |  | Correct Polarity |
| A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Climatic Conditions: Temperature: |  |  |  |  |  |  |  |  |  |  |  | Humidity: |  |  |  |  |  |  |  |
| Test Instruments |  | Make |  |  |  |  | Model |  |  |  |  | Serial Number |  |  |  |  | Calibration Cert |  |  |
| Insulation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hi Pot |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ductor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| HI POT TEST |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test | Insulation Before |  |  | Volts |  |  |  | Duration |  |  |  |  | Leakage Amps |  |  |  |  | Insulation After |  |
| A-B |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B-C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A-C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A-E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B-E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C-E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TERMINATION CHECK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| END | Check |  |  | A Phase |  |  |  | B Phase |  |  |  |  | C Phase |  |  |  |  | Earth |  |
| ###### A | Ductor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Bolt Torque |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ###### B | Ductor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Bolt Torque |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  |  | Tested By: Print Name: Sign: |  |  |  |  |  |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |  |  |  |  |  |

# ET 3	EARTH GRID INSPECTION & TEST REPORT

| SUBSTATION OR FIELD LOCATION: |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Connecting Cables Installation Checks |  |  |  | Comments |  |  |  |
| Correctly Routed: |  |  |  |  |  |  |  |
| Correctly Supported: |  |  |  |  |  |  |  |
| Correct Bend Radii: |  |  |  |  |  |  |  |
| Lugs Correct Size & Secure: |  |  |  |  |  |  |  |
| Connections Secure: |  |  |  |  |  |  |  |
| As per Drawings & Spec: |  |  |  |  |  |  |  |
| Test Instrument | Make |  | Model |  | Serial Number |  | Calibration Cert |
| Test |  | OHMS |  | Comment |  |  |  |
| Earth Grid |  |  |  |  |  |  |  |
| Reading 1 |  |  |  |  |  |  |  |
| Reading 2 |  |  |  |  |  |  |  |
| Reading 3 |  |  |  |  |  |  |  |
| Reading 4 |  |  |  |  |  |  |  |
| Average |  |  |  |  |  |  |  |
| Earth Conductor - electrode |  |  |  |  |  |  |  |
| Fences to Grid |  |  |  |  |  |  |  |
| Gates to Grid |  |  |  |  |  |  |  |
| Switchgear to Grid |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |
| Inspection and Test Date: |  | Tested By: Print Name: Sign: |  |  |  | Confirmed By: Print Name: Sign: |  |
| Anglo Supervisor Print Name: Sign: |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |

# ET 4	TRANSFORMER INSPECTION AND TEST REPORT (Page1 of 2)

| TRANSFORMER: |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Manufacturer: |  |  |  |  |  |  | % Impedience: |  |  |  |  |  |
| Type: |  |  |  |  |  |  | Type of Cooling: |  |  |  |  |  |
| Rating: |  |  |  |  |  |  |  |  |  |  |  |  |
| Primary Voltage: |  |  |  |  |  |  | Primary Amps: |  |  |  |  |  |
| Serial No: |  |  |  |  |  |  |  |  |  |  |  |  |
| Location: |  |  |  |  |  |  |  |  |  |  |  |  |
| Vector Group: |  |  |  |  |  |  |  |  |  |  |  |  |
| ACTIVITY |  |  |  |  |  |  | RESULT/COMMENT |  |  |  |  |  |
| 1. Transit packing removed from breather and vent |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Check, tighten all bolts. Ensure no leaks |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Check all insulators for cracks and chips |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Transformer positioned correctly |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Transformer bolted down correctly |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. Oil Samples from bottom of Transformer |  |  |  |  |  |  | (use test report ET 7) |  |  |  |  |  |
| 7. Oil Samples from top up oil drums |  |  |  |  |  |  | (use test report ET 7) |  |  |  |  |  |
| 8. With all valves open, check oil levels |  |  |  |  |  |  |  |  |  |  |  |  |
| 9. If sealed Transformer, check correct gas pressure |  |  |  |  |  |  |  |  |  |  |  |  |
| 10. Check Tap changer for correct movement |  |  |  |  |  |  |  |  |  |  |  |  |
| 11. Temperature Sensor fitted and connected |  |  |  |  |  |  |  |  |  |  |  |  |
| 12. Buchholz fitted and connected |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Instrument |  | Make |  | Model |  |  |  | Serial Number |  |  | Calibration Cert |  |
| Insulation |  |  |  |  |  |  |  |  |  |  |  |  |
| Hi Pot |  |  |  |  |  |  |  |  |  |  |  |  |
| Ductor |  |  |  |  |  |  |  |  |  |  |  |  |
| Continuity |  |  |  |  |  |  |  |  |  |  |  |  |
| Megger and High Voltage Test |  |  | Ambient Temperature |  |  |  |  |  |  | Humidity |  |  |
| Winding Temperature: oC |  |  |  |  |  |  |  |  |  |  |  |  |
| Element | Insulation Before |  | High Voltage |  |  |  |  |  |  |  |  | Insulation After |
|  |  |  | Voltage |  | Duration |  |  |  | Leakage Current |  |  |  |
| HV – LV & Tank |  |  |  |  |  |  |  |  |  |  |  |  |
| LV – HV & Tank |  |  |  |  |  |  |  |  |  |  |  |  |
| HV LV |  |  |  |  |  |  |  |  |  |  |  |  |
| Winding Resistance |  |  |  |  |  |  |  |  |  |  |  |  |
| Primary |  |  |  |  |  |  |  |  |  |  |  |  |
| A – B | A – C |  | B – C |  |  | A – N |  |  |  | B – N |  | C – N |
| Secondary |  |  |  |  |  |  |  |  |  |  |  |  |
| A – B | A – C |  | B – C |  |  | A – N |  |  |  | B – N |  | C - N |
| Voltage |  |  |  |  |  |  |  |  |  |  |  |  |
| Tap | 1 |  | 2 |  |  | 3 |  |  |  | 4 |  | 5 |
| Phase - Phase |  |  |  |  |  |  |  |  |  |  |  |  |
| Phase - Earth |  |  |  |  |  |  |  |  |  |  |  |  |
| Element | A Phase |  | B Phase |  |  | C Phase |  |  |  | Neutral |  | Earth |
| Ductor |  |  |  |  |  |  |  |  |  |  |  |  |
| Bolt Torque |  |  |  |  |  |  |  |  |  |  |  |  |

# ET 4	TRANSFORMER INSPECTION AND TEST REPORT (Page2 of 2)

| Bucholz Device |  |  |  |
| --- | --- | --- | --- |
| Manufacturer |  | Serial No. |  |
| Type |  |  |  |
| Gas |  | Surge |  |
| Temperature Device |  |  |  |
| Manufacturer |  | Serial No. |  |
| Type |  |  |  |
| Alarm oC |  | Trip oC |  |
| Breather |  |  |  |
| Silica Gel Colour |  | Oil Seal |  |
| COMMENTS: |  |  |  |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |

# ET 5	SWITCHGEAR INSPECTION AND TEST REPORT	(Page1 of 2)

| LOCATION: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Circuit Designation |  |  |  |  |  |
| Equipment Make: |  |  | CB Make: |  |  |
| Type: |  |  | Type: |  |  |
| Serial No: |  |  | Serial No: |  |  |
| Voltage: |  |  | Amps: |  |  |
| Short Circuit Withstand Time: |  |  | Short Circuit Withstand Current: |  |  |
| ## INSPECTION |  |  |  |  |  |
| ## Checkpoint |  | ## Condition |  | ## Comments |  |
| Rack in/out Mechanism |  |  |  |  |  |
| Main Contacts |  |  |  |  |  |
| Arc Chutes |  |  |  |  |  |
| Charging Spring |  |  |  |  |  |
| Electrical Operation |  |  |  |  |  |
| Manual Operation |  |  |  |  |  |
| Trip Mechanism |  |  |  |  |  |
| Primary Stabs |  |  |  |  |  |
| Safety Shutters |  |  |  |  |  |
| Cleanliness |  |  |  |  |  |
| Interlocks Earth/Lockout/Isolation |  |  |  |  |  |
| Breaker Alignment |  |  |  |  |  |
| Vacuum Condition |  |  |  |  |  |
| Gas Pressure |  |  |  |  |  |
| Oil Levels |  |  |  |  |  |
| Insulation Resistance |  |  |  |  |  |
| Voltage V Phase to Phase |  |  | Voltage V Phase to Phase |  |  |
| Before HV Test |  |  |  |  |  |
| A – B | A – C | B – C | A – E | B – E | C – E |
| After HV Test |  |  |  |  |  |
| A – B | A – C | B – C | A – E | B – E | C – E |

# ET 5	SWITCHGEAR INSPECTION AND TEST REPORT	(Page2 of 2)

| HIGH VOLTAGE TEST |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Between | Voltage |  | Duration |  | Leakage Current |
| A – B + C + E |  |  |  |  |  |
| B – A + C + E |  |  |  |  |  |
| C – A + B + E |  |  |  |  |  |
| A, B, C Contacts Parallelled, CB Open |  |  |  |  |  |
| VT Insulation Resistance |  |  |  |  |  |
| Primary to Secondary + Earth: |  |  | Secondary to Earth: |  |  |
| Ductor |  |  |  |  |  |
| Element | A Phase |  | B Phase |  | C Phase |
| CB Contacts |  |  |  |  |  |
| Busbar Joints |  |  |  |  |  |
| Inspection and Test Date: |  | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |  |
| Anglo Supervisor Print Name: Sign: |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |

# ET 6	DISTRIBUTION EQUIPMENT FUNCTION CHECK LIST

| LOCATION: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Circuit / Swichboard Designation: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TRIPPING (Electrical): Fuse Size: Amps: Volts: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Emergency Trip |  |  |  | O/C A Phase |  |  |  |  |  |  | Buchholz Surge |  |  |  |  |
| Local Control Sw. |  |  |  | O/C C Phase |  |  |  |  |  |  | Winding Temp. |  |  |  |  |
| Remote Control Sw. |  |  |  | Earth Fault |  |  |  |  |  |  | Oil Temp. |  |  |  |  |
| Remote P/B |  |  |  | Differential |  |  |  |  |  |  | Restricted E/F |  |  |  |  |
| Trip Relay |  |  |  | Reverse Power |  |  |  |  |  |  | Standby E/F |  |  |  |  |
| Busbar Earth |  |  |  | Circuit Earth |  |  |  |  |  |  | Intertrip |  |  |  |  |
| TRIPPING (Mechanical) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mechanical Trip Button |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| O/L Relay –Long Time Delay Set |  |  | Op |  |  | Times A |  |  |  | B |  |  |  | C |  |
| O/L Relay – Instantaneous Set |  |  | Op |  |  | Times |  |  |  |  |  |  |  |  |  |
| CLOSING (Control): Fuse Size: Amps: Volts: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Local |  |  | Remote |  |  |  |  |  |  |  | Local |  |  | Remote |
| Racking Sw. |  |  |  |  |  |  |  | Service Position |  |  |  |  |  |  |  |
| Local/Remote Sw. |  |  |  |  |  |  |  | Busbar E |  |  |  |  |  |  |  |
| Local Contact Sw. |  |  |  |  |  |  |  | Circuit E |  |  |  |  |  |  |  |
| CLOSING (Power): Fuse Size: Amps: Volts: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CB In Service Posn. |  |  |  |  |  |  | CB in Busbar E Posn. |  |  |  |  |  |  |  |  |
| CB in Circuit E Posn. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INDICATION: Fuse Size: Amps: Volts: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Op |  |  | Test |  |  |  | Op |  |  |  | Test |  |  |
| Off |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| On |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Auto Trip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Trip Healthy |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Panel Voltmeter |  |  |  |  |  |  | Panel Ammeter |  |  |  |  |  |  |  |  |
| ALARMS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Buchholz Gas |  |  |  |  |  |  | Alarm On All Protection Trips |  |  |  |  |  |  |  |  |
| Overtemperature |  |  |  |  |  |  | 110 V Control Supply |  |  |  |  |  |  |  |  |
| ## MISCELLANEOUS TESTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Oil Level OCB Tank: |  |  |  |  |  |  | Closing Coil Current: Amps: |  |  |  |  |  |  |  |  |
| Oil level VT Tank: |  |  |  |  |  |  | Tripping Coil Current: Amps: |  |  |  |  |  |  |  |  |
| ## FOR VACUUM INTERRUPTERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| With Interrupters Closed Gap Measured To Be: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Single Line Diagram |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Schematic Diagram |  |  |  |  |  |  | Wiring Diagram |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ET 6 DISTRIBUTION EQUIPMENT FUNCTION CHECK LIST SIGNOFF |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  | Inspected By: Print Name: Sign: |  |  |  |  |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |  |  |  |

# ET 7		TRANSFORMER OIL TEST REPORT

| LOCATION: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Oil Type: |  |  |  | Oil Manufacturer: |  |  |  |  |  |
| Test Equipment Used: |  |  |  |  |  |  |  |  |  |
| Test Carried Out: |  |  |  |  |  |  |  |  |  |
| TEST RESULTS: |  |  |  |  |  |  |  |  |  |
| Batch No. Or Equipment to be Used In: | Clarity |  | Colour |  |  | Crackle Test |  | 40 kV For 1 Min | Breakdown Voltage |
| COMMENTS: |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  | Inspected By: Print Name: Sign: |  |  |  |  | Confirmed By: Print Name: Sign: |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |

# ET 8	CONVEYOR ELECTRICAL COMMISSIONING INSPECTION AND TEST REPORT

| LOCATION: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conveyor No: |  |  |  |  |  |  |  |  |  |
| Supplied From: |  |  |  |  | MCC Module: |  |  |  |  |
| Control Fuse Size: Amps |  |  |  |  | Volts |  |  |  |  |
| Power Fuse Size: Amps |  |  |  |  | Volts |  |  |  |  |
| Power Circuit Resistance |  |  |  |  |  |  |  |  |  |
| Module Heater |  |  |  |  | Motor Heater |  |  |  |  |
| Thermal Overloads Heater No. Setting |  |  |  |  | Amps |  |  |  |  |
| Electronic Overload Type Setting |  |  |  |  | Amps |  |  |  |  |
| CT Type | Function |  |  |  | Ratio |  |  | Class |  |
| CT Type | Function |  |  |  | Ratio |  |  | Class |  |
| Ammeter Range |  |  |  |  | Ratio |  |  |  |  |
| ## CONTROL AND PROTECTION |  |  |  |  |  |  |  |  |  |
| Control Function |  | Auto |  |  |  | Manual |  |  |  |
|  |  | Start |  | Stop |  | Start |  |  | Stop |
| Local |  |  |  |  |  |  |  |  |  |
| Remote |  |  |  |  |  |  |  |  |  |
| ## PULLWIRE SWITCHES – Test Operation and Indication |  |  |  |  |  |  |  |  |  |
| 1 | 4 |  |  |  | 7 |  |  | 10 |  |
| 2 | 5 |  |  |  | 8 |  |  | 11 |  |
| 3 | 6 |  |  |  | 9 |  |  | 12 |  |
| ## BELT DRIFT SWITCHES – Test Operation and Indication |  |  |  |  |  |  |  |  |  |
| 1 | 4 |  |  |  | 7 |  |  | 10 |  |
| 2 | 5 |  |  |  | 8 |  |  | 11 |  |
| 3 | 6 |  |  |  | 9 |  |  | 12 |  |
| ## GENERAL CONTROL – Test Operation and Indication |  |  |  |  |  |  |  |  |  |
| Plant Emergency Stop |  |  |  |  | Underspeed |  |  |  |  |
| Blocked Chute 1 |  |  |  |  | Blocked Chute 2 |  |  |  |  |
| Incomplete Start |  |  |  |  | Thermistor |  |  |  |  |
| Metal Detector |  |  |  |  | Relay |  |  |  |  |
| Thermal O/L |  |  |  |  | Electronic O/L |  |  |  |  |
| Mcc Module Carriage I/Lock |  |  |  |  | Mcc Module Isolator |  |  |  |  |
| Test Switch |  |  |  |  |  |  |  |  |  |
| Belt Drift Timer secs |  |  |  |  | Start Warning Timer secs |  |  |  |  |
| Blocked Chute Timer secs |  |  |  |  | Brake Lift Timer secs |  |  |  |  |
| Run Up Timer secs |  |  |  |  |  |  |  |  |  |
| Schematic Diagram |  |  |  |  |  |  |  |  |  |
| Wiring / Termination Diagram |  |  |  |  |  |  |  |  |  |
| ## ALARMS – Test Operation and Indication |  |  |  |  |  |  |  |  |  |
| Overload |  |  |  |  |  |  |  |  |  |
| Thermistor |  |  |  |  | Underspeed |  |  |  |  |
| Brake Limit |  |  |  |  | Emergency Stop |  |  |  |  |
| Blocked Chute |  |  |  |  | Belt Drift |  |  |  |  |
| FAC Fault |  |  |  |  |  |  |  |  |  |
| Rotor Cubile O/Temp |  |  |  |  |  |  |  |  |  |
| ## INDICATION TEST |  |  |  |  |  |  |  |  |  |
| Ready |  |  |  |  | Running |  |  |  |  |
| ## LOAD TEST |  |  |  |  |  |  |  |  |  |
| Minimum Load Readings |  |  | Volts: |  |  |  | Amps: |  |  |
| Full Load Readings |  |  | Volts: |  |  |  | Amps: TPH |  |  |
| Full Belt Start |  |  | Volts (min): |  |  |  | Amps (Max): |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |
| ET 8 CONVEYOR ELECTRICAL COMMISSIONING INSPECTION AND TEST REPORT SIGNOFF |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  | Inspected By: Print Name: Sign: |  |  |  | Confirmed By: Print Name: Sign: |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |

# ET 9	OVERCURRENT AND EARTH FAULT PROTECTION RELAYS (Page1 of 2)

| LOCATION: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CIRCUIT DESIGNATION: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System Voltage |  |  |  |  |  |  |  | Rated Current |  |  |  |  |  |  |  |
| Relay Type |  |  |  |  |  |  |  | Manufacturer |  |  |  |  |  |  |  |
| Relay Model |  |  |  |  | DMT Sec |  |  |  |  |  | Figure |  |  |  |  |
| Element | Serial No. |  | Instantaneous |  |  |  |  |  |  | Overcurrent |  |  |  |  |  |
|  |  |  | Range |  |  | Setting |  |  |  | Range |  | Setting |  | Time Setting |  |
| A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Earth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CURRENT TRANSFORMER MANUFACTURER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Elements |  | ## Serial No. |  | ## Ratio |  |  | ## Accuracy |  | ## Tap |  |  |  | ## Injection Tests |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ## Pri. Amps |  | ## Secs Amps |
| ## A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## B |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Earth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Neutral |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

# ET 9	OVERCURRENT AND EARTH FAULT PROTECTION RELAYS (Page2 of 2)

| ## SECONDARY INJECTION TESTS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Element | Setting |  | Pick-up Current |  |  | Operating Time at Rimes Relay Setting |  |  |  |  |  |  | Time Multipler |
|  |  |  |  |  |  | 2 |  | 5 |  |  | 10 |  |  |
| A | 50 or 100% |  |  |  |  |  |  |  |  |  |  |  | 1.0 |
|  | 50 or 100% |  |  |  |  |  |  |  |  |  |  |  | 0.5 |
| B | 50 or 100% |  |  |  |  |  |  |  |  |  |  |  | 1.0 |
|  | 50 or 100% |  |  |  |  |  |  |  |  |  |  |  | 0.5 |
| C | 50 or 100% |  |  |  |  |  |  |  |  |  |  |  | 1.0 |
|  | 50 or 100% |  |  |  |  |  |  |  |  |  |  |  | 0.5 |
| Earth | 50 or 100% |  |  |  |  |  |  |  |  |  |  |  | 1.0 |
| Ground | 50 or 100% |  |  |  |  |  |  |  |  |  |  |  | 0.5 |
| Instantaneous O/C |  | Relay Setting |  |  | Pick-up Current |  |  |  | Relay Setting |  |  | Pick-up Current |  |
| Trip Voltage |  |  |  |  |  |  | Function Test Fault Trip |  |  |  |  |  |  |
| Alarm Voltage |  |  |  |  |  |  | Function Test Alarm Trip |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  | Inspected By: Print Name: Sign: |  |  |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |  |  |

# ET 10 	AC MOTOR COMMISSSIONING TEST REPORT (Page1 of 2)

| LOCATION: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Motor: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Motor Serial No: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Motor Data: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Make: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power |  |  |  |  | Speed |  |  |  |  |  | Frame |  |  |  |  |
| Volts (R) |  |  |  |  | Amps (R) |  |  |  |  |  | Class |  |  |  |  |
| Volts (S) |  |  |  |  | Amps (S) |  |  |  |  |  | Enclosure |  |  |  |  |
| Test Equipment Used |  |  | Make |  |  |  | Model |  | Serial No. |  |  |  | Calibration Cert. |  |  |
| Insulation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Continuity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Continuity of Windings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Results |  |  | Stator |  |  |  | R – W |  | W – B |  |  |  | R – B |  |  |
|  |  |  | Rotor |  |  |  | A – B |  | B – C |  |  |  | C – A |  |  |
| Stator Winding Insulation Resistance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A – B |  | A – C |  |  | B – C |  |  | A – E |  |  | B – E |  |  | C - E |  |
| Rotor Winding Insulation Resistance Winding to Earth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Motor Stator Winding to Earth, with Cables connected Prior to Energising |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Motor Rotor Winding to Earth, with Cables connected Prior to Energising |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Volts Min. Load | R – W |  |  | R – B |  | B – W |  | Amps Min. Load |  | R |  | W |  |  | B |
| Volts Max. Load | R – W |  |  | R – B |  | B – W |  | Amps Min. Load |  | R |  | W |  |  | B |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

# ET 10 	AC MOTOR COMMISSSIONING TEST REPORT (Page2 of 2)

| Accelerating Resistors |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Stage | 1 | 2 | 3 |  | 4 |  | 5 | 6 |  | 7 | 8 | 9 |
| Timer |  |  |  |  |  |  |  |  |  |  |  |  |
| Ext Resis. (Total) |  |  |  |  |  |  |  |  |  |  |  |  |
| Max. Current |  |  |  |  |  |  |  |  |  |  |  |  |
| Min. Volts At |  |  |  |  |  |  |  |  |  |  |  |  |
| Brush Tension |  |  |  |  |  | Brush Grade |  |  |  |  |  |  |
| Thermistor |  |  |  | BRG Brinelling |  |  |  |  | 4 hr BRG Temp Test |  |  |  |
| Resistance |  |  |  | D.E. |  |  |  |  | D.E. |  |  |  |
| Relay Op. |  |  |  | N.D.E. |  |  |  |  | N.D.E. |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  | Inspected By: Print Name: Sign: |  |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |  |

# ET 11 SMALL MOTOR & ELECTRICAL EQUIPMENT COMMISIONING TEST REPORT

| LOCATION: |  |  |  |  |  |  |  |  | DRIVES: |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Motor, equipment Purpose | Make | Serial No. |  | Frame Size | Insul. Class | Encl. |  | hp or VA | RPM |  | Rotation Drv End | Megger WDG-E |  | O/L Setting | Volts |  |  | Amps |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Rated | F/L |  | Rated | N/L | F/L |
| Single Line Diagram |  |  |  |  |  |  |  |  |  | Schematic Diagrams |  |  |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  | Inspected By: Print Name: Sign: |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |  |  | Anglo Supervisor: Print Name: Sign: |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |

# ET 12 	MOTOR CONTROL CENTRE CUBICLE ELECTRICAL   INSPECTION AND TEST REPORT (Page1 of 2)

| LOCATION: |  |  | MCC ID: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Circuit Designation/Cubicle ID |  |  |  |  |  |  |  |
| Control Fuse Size Amps |  |  | Volts |  |  |  |  |
| Power Fuse Size Amps |  |  | Volts |  |  |  |  |
| Control Cable Size: |  |  |  |  |  |  |  |
| Power Cable Size: |  |  |  |  |  |  |  |
| Isolator Size: |  |  |  |  |  |  |  |
| Contactor Size: |  |  |  |  |  |  |  |
| Thermal Overloads Heater No. Setting |  |  | Amps |  |  |  |  |
| Time to Operate at 2 x setting Amps |  |  | A secs | B secs |  |  | C secs |
| Electronic Overload Type Setting |  |  | Amps |  |  |  |  |
| Time to Operate at 2x setting Amps |  |  | A secs | B secs |  |  | C secs |
| ## CURRENT TRANSFORMERS |  |  |  |  |  |  |  |
| Function |  | Ratio | Class |  |  | Ratio Check |  |
| Function |  | Ratio | Class |  |  | Ratio Check |  |
| Ammeter Range |  |  | Ratio |  |  |  |  |
| Tripping Circuit |  |  |  |  |  |  |  |
| Full Function Test of All Electrical Equipment |  |  |  |  |  |  |  |
| Earth Leakage Test |  |  |  |  |  |  |  |
| Timers | Details |  |  |  | Op Time Secs |  |  |
|  | Details |  |  |  | Op Time Secs |  |  |
|  | Details |  |  |  | Op Time Secs |  |  |
|  | Details |  |  |  | Op Time Secs |  |  |
|  | Details |  |  |  | Op Time Secs |  |  |
|  | Details |  |  |  | Op Time Secs |  |  |

# ET 12 	MOTOR CONTROL CENTRE CUBICLE ELECTRICAL   INSPECTION AND TEST REPORT (Page 2of 2)

| Check Labels |  |  |  |
| --- | --- | --- | --- |
| Check Ferruling |  |  |  |
| Check Fuse Strikers |  |  |  |
| Check Earth Connections |  |  |  |
| Single Line Diagram |  |  |  |
| Schematic Diagram |  |  |  |
| Wiring/Termination Diagram |  |  |  |
| COMMENTS: |  |  |  |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |

# ET 13		MISCELLANEOUS ELECTRICAL TEST REPORT

| LOCATION: |  |  |  |
| --- | --- | --- | --- |
| Equipment: |  |  |  |
| Equipment Serial No: |  |  |  |
| Equipment Data Rated Voltage: |  |  |  |
| Test Equipment Used: |  |  |  |
| Test Carried Out: Test Duration |  |  |  |
| Test Results: |  |  |  |
| Drawings: |  |  |  |
| COMMENTS: |  |  |  |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |

# ET 14	MISCELLANEOUS DRIVE COMMISSIONING TEST REPORT (Page1 of 2)

| LOCATION: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Drive Designation: |  |  |  |  |  |  |  |  |  |
| ## MOTOR CONTROL CENTRE |  |  |  |  |  |  |  |  |  |
| Control Fuse Size Amps Volts |  |  |  |  |  |  |  |  |  |
| Power Fuse Size Amps Volts |  |  |  |  |  |  |  |  |  |
| Module Heater |  |  |  |  |  |  |  |  |  |
| Isolator Interlocks |  |  |  |  |  |  |  |  |  |
| Contactor Coil Test P/B |  |  |  |  |  |  |  |  |  |
| Drive Indicator Lights |  |  |  |  |  |  |  |  |  |
| Thermal Overloads Heater No. Setting Amps |  |  |  |  |  |  |  |  |  |
| Time to Operate at 2 x setting Amps |  |  |  | A Sec |  | B Sec |  |  | C Sec |
| Electronic Overload Type Setting Amps |  |  |  |  |  |  |  |  |  |
| Time to Operate at 2 x setting |  |  |  | A Sec |  | B Sec |  |  | C Sec |
| ## CURRENT TRANSFORMERS |  |  |  |  |  |  |  |  |  |
| Function |  | Ratio |  |  | Class |  |  | Ratio Check |  |
| Function |  | Ratio |  |  | Class |  |  | Ratio Check |  |
| Ammeter Range |  |  |  |  | Ratio |  |  |  |  |
| ## CONTROL AND PROTECTION |  |  |  |  |  |  |  |  |  |
| Timers |  |  | Setting Secs |  |  |  | Op Time Secs |  |  |
|  |  |  | Settings Secs |  |  |  | Op Time Secs |  |  |
|  |  |  | Settings Secs |  |  |  | Op Time Secs |  |  |
|  |  |  | Settings Secs |  |  |  | Op Time Secs |  |  |
| Underspeed |  |  | Settings Secs |  |  |  | Op RPM RPM |  |  |
| Pressure |  |  | Setting Secs |  |  |  | Op Press kPa |  |  |
|  |  |  | Setting Secs |  |  |  | Op Press kPa |  |  |
|  |  |  | Setting Secs |  |  |  | Op Press kPa |  |  |
| Temperature |  |  | Setting Secs |  |  |  | Op Temp oC |  |  |
|  |  |  | Setting Secs |  |  |  | Op Temp oC |  |  |
|  |  |  | Setting Secs |  |  |  | Op Temp oC |  |  |

# ET 14	MISCELLANEOUS DRIVE COMMISSIONING TEST REPORT (Page2 of 2)

| ## LOAD TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Voltage At Motor Terminals | Dry Run Volts |  |  | Full Load Volts |
|  | Minimum During Starting on Full Load Volts |  |  |  |
| Current Drawn By Motor | Dry Run Volts |  |  | Full Load Amps |
|  | Maximum During Starting on Full Load Amps |  |  |  |
| Full Load Condition |  |  | Run up Time Secs |  |
| Single Line Diagram |  |  |  |  |
| Schematic Diagram |  |  | Wiring/Termination Diagram |  |
| COMMENTS: |  |  |  |  |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  |  | Confirmed By: Print Name: Sign: |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |  |

# ET 15 MOTOR CIRCUIT & ROTOR CABLE TEST SHEET (Page1 of 2)

(This test sheet is to be used for all motors tested, with the exception of replacement motors, which use ET 21)

| TICK | EARTH CONTINUITY TEST – MOTOR POWER CABLE |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1. Isolate supply. |  |  |  |
|  | 2. Set Ohm meter to zero Ohm with leads connected together. |  |  |  |
|  | 3. Connect a lead to main earth of MEN connection. |  |  |  |
|  | 4. Connect flying lead to all parts of installation required to be earthed. |  |  |  |
| LCS |  | Cable Gland |  | Door |
|  |  | Gland Plate |  | Earth bar/link |
|  |  | Gear Tray |  |  |
| Motor |  | Motor Frame |  | Gland Plate |
|  | 5. Disconnect main power cable and motor power cable earths from LCS earth bar. |  |  |  |
|  | 6. Connect meter between main power cable earth to motor power cable earth at LCS. Test and record result. |  |  |  |
|  | 7. Test that resistance does not exceed two (2) Ohms. |  |  |  |
|  | 8. Reconnect main power cable earth and motor power cable earth at LCS earth bar. |  |  |  |
|  | 9. Return supply isolator to original state. |  |  |  |

| TICK | INSULATION RESISTANCE TEST – MOTOR POWER CABLE |
| --- | --- |
|  | 1. Isolate supply. An HV Access permit is required for performing this test on 3 300V circuits. |
|  | 2. Ensure local isolator in field in ON (if test is conducted from MCC) |
|  | 3. Set meter to read insulation resistance. |
|  | 4. From the load side of contactor or at cable exit terminals from cubicle, test the main power cable by connecting meter lead between phases and earth, test at 500V. Test and record for each phase. |
|  | 5. Required result for this test shall be not less than one (1) meg Ohm. |
|  | 6. Return supply isolator to original state. |

| TICK | INSULATION RESISTANCE TEST – ROTOR CABLE |
| --- | --- |
|  | 1. Isolate supply. |
|  | 2. Disconnect rotor cables at rotor resistance cubicle. |
|  | 3. Lift brush gear on motor. |
|  | 4. Set meter to read insulation resistance. |
|  | 5. Connect leads between phases and earth, test at 500V. Test and record for each phase. |
|  | 6. Connect leads between phases. Test at 1 000V. Test and record for each phase. |
|  | 7. Required result for this test shall be not less than one (1) meg Ohm. |
|  | 8. Reset brush gear. Reseal motor terminals. |
|  | 9. Reconnect rotor cables at rotor resistance cubicle. |
|  | 10. Return isolator to original state. |

| EARTH CONTINUITY TEST – MOTOR POWER CABLE |  |  |  |
| --- | --- | --- | --- |
| MCC/MAIN SUPPLY TO MOTOR | Reading Ohms | Date | Tested By: |

# ET 15 MOTOR CIRCUIT & ROTOR CABLE TEST SHEET (Page2 of 2)

| ## INSULATION RESISTANCE TEST – MOTOR POWER CABLE |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Test Voltage | Reading Megohms | Date | Tested By |
| Core Red to cable earth |  |  |  |  |
| Core White to cable earth |  |  |  |  |
| Core Blue to cable earth |  |  |  |  |

| ## EARTH CONTINUITY TEST – ROTOR CABLE |  |  |  |
| --- | --- | --- | --- |
| Cable No. | Reading Ohms | Date | Tested By |

| INSULATION RESISTANCE TEST – ROTOR CABLE |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable No. | Test Voltage | Reading Megohms | Date | Tested By |
| Core Red to White |  |  |  |  |
| Core Red to Blue |  |  |  |  |
| Core Red to cable earth |  |  |  |  |
| Core White to cable earth |  |  |  |  |
| Core Blue to cable earth |  |  |  |  |

If readings are below/above acceptable level, record the fault found below.

| Was fault rectified? | YES |  | NO |
| --- | --- | --- | --- |
| If NO, why? |  |  |  |
| If YES, record new results on another test sheet and attach new test sheet to this test sheet. |  |  |  |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |

# ET 16 LIGHTING CIRCUIT INSPECTION AND TEST SHEET (Page1 of 2)

(This test sheet is to be used for all lighting circuits, new or modified)

| TICK | LIGHTING CIRCUIT – EARTH CONTINUITY TEST |
| --- | --- |
|  | 1. Isolate supply and disconnect the earth conductors of the portion of the installation under test. |
|  | 2. Set Ohm meter to zero Ohm with leads connected together. |
|  | 3. Connect a lead to cable earth. |
|  | 4. Using a flying lead, a copper nail attached to lead through a length of PVC conduit, connect nail on flying lead to exposed metal surface of light fitting. Test and record result. |
|  | 5. Test result does not exceed two (2) Ohms. |
|  | 6. Reconnect earth circuit conductors. |
|  | 7. Return supply isolator to original state. |

| TICK | ## LIGHTING CIRCUIT – INSULATION RESISTANCE TEST |
| --- | --- |
|  | 1. Remove fuse or turn off circuit breaker protecting circuit under test. |
|  | 2. Ensure all switched are on. |
|  | 3. Disconnect neutral conductor of circuit under test from neutral bar. |
|  | 4. Join circuit conductors under test together. (Active and neutral). |
|  | 5. Set meter to read Meg Ohm. 500V for 240 VAC. |
|  | 6. Connect test lead between main earthing conductor at earth bar and joined circuit conductors. Test and record result. |
|  | 7. Required result for this test shall be not less than 1 Meg Ohm. |
|  | 8. If insulation resistance is less than 1 Meg Ohm, test circuit wiring and appliances separately. |
|  | 9. Disconnect test leads, separate circuit conductors and reconnect circuit neutral conductors. |
|  | 10. Return fuse or supply isolator to original state. |

| ## LUMINAIRE CHECKS |  |  | ## EMERGENCY LIGHTING |  |  |
| --- | --- | --- | --- | --- | --- |
| Installed to drawing |  |  | Installed to drawing |  |  |
| Correctly mounted |  |  | Correctly mounted |  |  |
| Correct type |  |  | Correct type |  |  |
| Correct size |  |  | Correct size |  |  |
| Initial survey done |  |  | Operate correctly |  |  |
| Adjustments made |  |  |  |  |  |
| Final survey complete |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  |  | Confirmed By: Print Name: Sign: |  |
| Anglo Supervisor Print Name: Sign: |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |

# ET 16 LIGHTING CIRCUIT INSPECTION AND TEST SHEET (Page2 of 2)

LIGHTING CIRCUIT – EARTH CONTINUITY TEST

CCT No./Cable No.________________from distribution board.

Ohms reading in this test is the total from distribution board to each light listed.

| Light No. Prefix |  | Reading Ohms | Date | Tested By |
| --- | --- | --- | --- | --- |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |
| To Light No. |  |  |  |  |

LIGHTING CIRCUIT – INSULATION RESISTANCE TEST

CCT No./Cable No.__________________

| Core Red & Black to E |  | Reading Megohms |  | Date |  | Tested By |
| --- | --- | --- | --- | --- | --- | --- |
| If reading is low, record the fault found: |  |  |  |  |  |  |
| Core Red & Black to E |  | Reading Megohms |  | Date |  | Tested By |
| If reading low, record after fault repaired: |  |  |  |  |  |  |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  |  |  | Confirmed By: Print Name: Sign: |  |
| Anglo Supervisor Print Name: Sign: |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |

# ET 17		GPO CIRCUIT TEST SHEET (Page1 of 2)

GPO CIRCUIT – EARTH CONTINUITY TEST

| Instrument Type |  | Make | Model | Serial No | Calibration Cert. |
| --- | --- | --- | --- | --- | --- |
| Continuity |  |  |  |  |  |
| TICK |  |  |  |  |  |
|  | 1. Isolate supply and disconnect the earth conductor of the portion of the installation under test. |  |  |  |  |
|  | 2. Set Ohm meter to zero Ohm with leads connected together. |  |  |  |  |
|  | 3. Using the flying lead, connect to earth on male 3 pin plug top and connect plug top to GPO. |  |  |  |  |
|  | 4. Connect meter lead between cable earth at source and flying lead. Test and record result. |  |  |  |  |
|  | 5. Test result does not exceed two (2) Ohms. (Go to next GPO on circuit and repeat). |  |  |  |  |
|  | 6. Reconnect earth circuit conductors. |  |  |  |  |
|  | 7. Return supply isolator to original state. |  |  |  |  |

GPO CIRCUIT – INSULATION RESISTANCE TEST

| Instrument Type |  | Make | Model | Serial No | Calibration Cert. |
| --- | --- | --- | --- | --- | --- |
| Insulation |  |  |  |  |  |
| TICK |  |  |  |  |  |
|  | 1. Remove fuse or turn off circuit breaker protecting circuit under test. |  |  |  |  |
|  | 2. Ensure all switches are on. |  |  |  |  |
|  | 3. Disconnect neutral conductor of circuit under test from neutral bar. |  |  |  |  |
|  | 4. Join circuit conductors, under test, together (Active and neutral). |  |  |  |  |
|  | 5. Set meter to read Meg Ohm. 500V for 240 VAC. |  |  |  |  |
|  | 6. Connect meter lead between main earthing conductor at earth bar and joined circuit conductors. Test and record result. |  |  |  |  |
|  | 7. Required result for this test shall be not less than 1 Meg Ohm. |  |  |  |  |
|  | 8. If insulation resistance is less than 1 Meg Ohm test circuit wiring and appliances separately. |  |  |  |  |
|  | 9. Disconnect test leads, separate circuit conductors and reconnect circuit neutral conductors. |  |  |  |  |
|  | 10. Return fuse or supply isolator to original state. |  |  |  |  |

GPO CIRCUIT – INSTALLATION INSPECTION

| TICK |  |
| --- | --- |
|  | 1. Cable check complete. |
|  | 2. Correct type and size. |
|  | 3. Correctly mounted. |

GPO CIRCUIT – EARTH CONTINUITY TEST

CCT No./Cable No. ______________________from distribution board.

| CB No. | Ohms | CB No. | Ohms |
| --- | --- | --- | --- |
| To GPO No. |  | To GPO No. |  |
| To GPO No. |  | To GPO No. |  |
| To GPO No. |  | To GPO No. |  |
| To GPO No. |  | To GPO No. |  |

| Inspection and Test Date: | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |
| --- | --- | --- | --- |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |

# ET 17		GPO CIRCUIT TEST SHEET (Page2 of 2)

GPO CIRCUIT – INSULATION RESISTANCE TEST

CCT No./Cable No._______________________from distribution board.

| From CB No. | Reading Megohms | Polarity Test Result |
| --- | --- | --- |
| Core Red to Black |  |  |
| Core Red to Earth |  |  |
| Core Black to Earth |  |  |

GPO CIRCUIT – EARTH CONTINUITY TEST

CCT No./Cable No. ______________________from distribution board.

| CB No. | Ohms | CB No. | Ohms |
| --- | --- | --- | --- |
| To GPO No. |  | To GPO No. |  |
| To GPO No. |  | To GPO No. |  |
| To GPO No. |  | To GPO No. |  |
| To GPO No. |  | To GPO No. |  |

GPO CIRCUIT – INSULATION RESISTANCE TEST

CCT No./Cable No._______________________from distribution board.

| From CB No. | Reading Megohms | Polarity Test Result |
| --- | --- | --- |
| Core Red to Black |  |  |
| Core Red to Earth |  |  |
| Core Black to Earth |  |  |

| Inspection and Test Date: | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |
| --- | --- | --- | --- |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |

# ET 18	WELDING OUTLET CIRCUIT TEST SHEET (Page1 of 2)

WELDING OUTLET CIRCUIT – EARTH CONTINUITY TEST

| Instrument Type |  | Make | Model | Serial No | Calibration Cert. |
| --- | --- | --- | --- | --- | --- |
| Continuity |  |  |  |  |  |
| TICK |  |  |  |  |  |
|  | 1. Isolate supply and disconnect the earth conductor of the portion of the installation under test. |  |  |  |  |
|  | 2. Set Ohm meter to zero Ohm with leads connected together. |  |  |  |  |
|  | 3. Using the flying lead, connect to earth pin of welding outlet. |  |  |  |  |
|  | 4. Connect meter lead between cable earth and flying lead. Test and record result. |  |  |  |  |
|  | 5. Test result does not exceed two (2) Ohms. |  |  |  |  |
|  | 6. Reconnect earth circuit conductors. |  |  |  |  |
|  | 7. Return supply isolator to original state. |  |  |  |  |

WELDING OUTLETS CIRCUIT – INSULATION RESISTANCE TEST

| Instrument Type |  | Make | Model | Serial No | Calibration Cert. |
| --- | --- | --- | --- | --- | --- |
| Insulation |  |  |  |  |  |
| TICK |  |  |  |  |  |
|  | 1. Remove fuse or turn off circuit breaker protecting circuit under test. |  |  |  |  |
|  | 2. Ensure all switches are on. |  |  |  |  |
|  | 3. Disconnect neutral conductor of circuit under test from neutral bar. |  |  |  |  |
|  | 4. Set meter to read Meg Ohm. 500V for 240 VAC OR 1 000v for 415 VAC. |  |  |  |  |
|  | 5. Connect test lead between earth and phases. Test and record for each phase. |  |  |  |  |
|  | 6. Repeat for neutral. |  |  |  |  |
|  | 7. Connect leads between earth and neutral. Test and record. |  |  |  |  |
|  | 8. Connect leads between phases. Test and record each result. |  |  |  |  |
|  | 9. Required result for this test shall be not less than one (1) mega Ohm. |  |  |  |  |
|  | 10. Disconnect test leads and reconnect circuit neutral conductors. Return supply to original state. |  |  |  |  |

WELDING OUTLET CIRCUIT – EARTH CONTINUITY TEST

| Welding Outlet No |  | Reading Ohms |  |
| --- | --- | --- | --- |
| Date |  | Tested By |  |

# ET 18 WELDING OUTLET CIRCUIT TEST SHEET (Page2 of 2)

WELDING OUTLET CIRCUIT – INSULATION RESISTANCE TEST

|  | ## Test Voltage | Reading Megohms | Date | Tested By |
| --- | --- | --- | --- | --- |
| Core Red to White |  |  |  |  |
| Core Red to Blue |  |  |  |  |
| Core White to Blue |  |  |  |  |
| Core Red to Cable Earth |  |  |  |  |
| Core White to Cable Earth |  |  |  |  |
| Core Blue to Cable Earth |  |  |  |  |
| Core Red to Neutral |  |  |  |  |
| Core White to Neutral |  |  |  |  |
| Core Blue to Neutral |  |  |  |  |
| Neutral to Cable Earth |  |  |  |  |

If reading is below/above acceptable level, record fault found below and fill out new sheet when fault repaired.  Attach new sheet to this sheet.

WELDING OUTLET CIRCUIT – EARTH CONTINUITY TEST

| Welding Outlet No |  | Reading Ohms |  |
| --- | --- | --- | --- |
| Date |  | Tested By |  |

WELDING OUTLET CIRCUIT – INSULATION RESISTANCE TEST

|  | ## Test Voltage | Reading Megohms | Date | Tested By |
| --- | --- | --- | --- | --- |
| Core Red to White |  |  |  |  |
| Core Red to Blue |  |  |  |  |
| Core White to Blue |  |  |  |  |
| Core Red to Cable Earth |  |  |  |  |
| Core White to Cable Earth |  |  |  |  |
| Core Blue to Cable Earth |  |  |  |  |
| Core Red to Neutral |  |  |  |  |
| Core White to Neutral |  |  |  |  |
| Core Blue to Neutral |  |  |  |  |
| Neutral to Cable Earth |  |  |  |  |

If reading is below/above acceptable level, record fault found below and fill out new sheet when fault repaired.  Attach new sheet to this sheet.

| Inspection and Test Date: | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |
| --- | --- | --- | --- |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |

# ET 19  	HIGH VOLTAGE POWERLINES AND SWITCHYARDS INSPECTION SHEET

| ###### Item |  | Pass |  | Fail | Comment |  |
| --- | --- | --- | --- | --- | --- | --- |
| Span Distances |  |  |  |  |  |  |
| Conductor Sag |  |  |  |  |  |  |
| Insulator Condition |  |  |  |  |  |  |
| All Hardware Correctly Mounted |  |  |  |  |  |  |
| Earth Switches on Correct Side of Isolation Switches |  |  |  |  |  |  |
| Connections Correctly Made and Secure |  |  |  |  |  |  |
| Correct Operation of all Switchgear |  |  |  |  |  |  |
| Correct Operation of all Interlocks |  |  |  |  |  |  |
| Signage for Operational Voltage |  |  |  |  |  |  |
| Signage for Switchgear identification |  |  |  |  |  |  |
| Height signage for aerials crossing roads |  |  |  |  |  |  |
| Signage for Electrical buried services |  |  |  |  |  |  |
| Electrical Insulation tests Documented |  |  |  |  |  |  |
| Site Single lines updated & available |  |  |  |  |  |  |
| Protection settings checked against design |  |  |  |  |  |  |
| Comments |  |  |  |  |  |  |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  |  |  |  | Confirmed By: Print Name: Sign: |
| Anglo Supervisor Print Name: Sign: |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |

Forward copy to the Electrical Engineering Manager & file original in Electrical Library.

# ET 20	HIGH VOLTAGE AERIALS AND SWITCHYARD TEST SHEET

| CIRCUIT NO: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Resistance Test |  |  |  |  |  |  |  |  | DC High Voltage |  |  |  |  |  |  |  |  |  |
|  |  | Before HV |  |  | After HV |  |  |  | Conductor Polarity: |  |  |  |  |  |  |  |  |  |
| Voltage |  |  |  |  |  |  |  |  | Phase Colour | 1 |  |  | 2 |  | 3 |  | 4 |  |
| Time |  |  |  |  |  |  |  |  |  | Microamps |  |  | Microamps |  | Microamps |  | Microamps |  |
|  | MegOhms |  | MegOhms | MegOhms |  |  | MegOhms |  |  | kV |  |  |  |  |  |  |  |  |
| 1 – Earth |  |  |  |  |  |  |  |  |  | kV |  |  |  |  |  |  |  |  |
| 2 – Earth |  |  |  |  |  |  |  |  |  | kV |  |  |  |  |  |  |  |  |
| 3 – Earth |  |  |  |  |  |  |  |  |  | kV |  |  |  |  |  |  |  |  |
| 1 – 2 |  |  |  |  |  |  |  |  |  | kV |  |  |  |  |  |  |  |  |
| 2 – 3 |  |  |  |  |  |  |  |  |  | kV |  |  |  |  |  |  |  |  |
| 1 – 3 |  |  |  |  |  |  |  |  | (MAX) | kV |  |  |  |  |  |  |  |  |
| Nett - Earth |  |  |  |  |  |  |  |  |  | 15 sec |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 30 sec |  |  |  |  |  |  |  |  |
| DC HIGH VOLTAGE TEST PILOT |  |  |  |  |  |  |  |  |  | 45 sec |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 1 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 2 min |  |  |  |  |  |  |  |  |
| M I |  |  |  |  |  |  |  |  |  | 3 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 4 min |  |  |  |  |  |  |  |  |
| C R |  |  |  |  |  |  |  |  |  | 5 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 6 min |  |  |  |  |  |  |  |  |
| O A |  |  |  |  |  |  |  |  |  | 7 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 8 min |  |  |  |  |  |  |  |  |
| M P |  |  |  |  |  |  |  |  |  | 9 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 10 min |  |  |  |  |  |  |  |  |
| S |  |  |  |  |  |  |  |  |  | 11 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 12 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 13 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 14 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 15 min |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Set Control Voltage to Zero, Reverse Ammeter |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | kV | A |  | kV | A | kV | A | kV | A |
|  |  |  |  |  |  |  |  |  | 1 min |  |  |  |  |  |  |  |  |  |
| 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 |  |  |  |  |  |  |  |  | Use Rubber Gloves Ground Tested Cable, Disconnect Tester |  |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  |  |  | Inspected By: Print Name: Sign: |  |  |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |  |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |  |  |  |  |  |  |

# ET 21		BATTERY CHARGER TEST SHEET (Page1 of 2)

| Type No |  | Serial No |  |
| --- | --- | --- | --- |
| Location |  | Equipment No |  |
| Rating | volts |  |  |
|  | amps |  |  |
| VISUAL INSPECTION |  |  |  |
| Voltmeter |  | Ammeter |  |
| Circuit Breakers |  | Labels |  |
| Connections |  | General Condition |  |
| FUNCTION TESTS |  |  |  |
| Voltmeter |  | Ammeter |  |
| Charger Fail |  | DC C/C O/local trip | amps |
| Under Voltage set at | volts | Over Voltage Set at | volts |
| Earth Fault Alarm |  | Electrolyte Low Alarm |  |
| Float Volts set at | volts | Boost Volts set at | volts |
| Charge Current Limit | amps |  |  |
| COMMENTS: |  |  |  |

# ET 21		 BATTERY TEST SHEET (Page2 of 2)

| Location |  | Equipment No |  |
| --- | --- | --- | --- |
| Function |  | Battery Volts |  |
| Date |  | Battery Capacity |  |

| Cell No. | Volts | SPG | Remarks |  | Cell No. |  | Volts |  | SPG | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  | 29 |  |  |  |  |  |
| 2 |  |  |  |  | 30 |  |  |  |  |  |
| 3 |  |  |  |  | 31 |  |  |  |  |  |
| 4 |  |  |  |  | 32 |  |  |  |  |  |
| 5 |  |  |  |  | 33 |  |  |  |  |  |
| 6 |  |  |  |  | 34 |  |  |  |  |  |
| 7 |  |  |  |  | 35 |  |  |  |  |  |
| 8 |  |  |  |  | 36 |  |  |  |  |  |
| 9 |  |  |  |  | 37 |  |  |  |  |  |
| 10 |  |  |  |  | 38 |  |  |  |  |  |
| 11 |  |  |  |  | 39 |  |  |  |  |  |
| 12 |  |  |  |  | 40 |  |  |  |  |  |
| 13 |  |  |  |  | 41 |  |  |  |  |  |
| 14 |  |  |  |  | 42 |  |  |  |  |  |
| 15 |  |  |  |  | 43 |  |  |  |  |  |
| 16 |  |  |  |  | 44 |  |  |  |  |  |
| 17 |  |  |  |  | 45 |  |  |  |  |  |
| 18 |  |  |  |  | 46 |  |  |  |  |  |
| 19 |  |  |  |  | 47 |  |  |  |  |  |
| 20 |  |  |  |  | 48 |  |  |  |  |  |
| 21 |  |  |  |  | 49 |  |  |  |  |  |
| 22 |  |  |  |  | 50 |  |  |  |  |  |
| 23 |  |  |  |  | 51 |  |  |  |  |  |
| 24 |  |  |  |  | 52 |  |  |  |  |  |
| 25 |  |  |  |  | 53 |  |  |  |  |  |
| 26 |  |  |  |  | 54 |  |  |  |  |  |
| 27 |  |  |  |  | 55 |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  |  |  |
| Discharge Test Result |  |  |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  | Inspected By: Print Name: Sign: |  |  |  | Confirmed By: Print Name: Sign: |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |

# ET 22 CONTROL CABLE INSPECTION AND TEST SHEET (Page1 of 2)

| PROJECT TITLE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cable Number |  |  |  |  |  |  |  | Cable Type |  |  |  |  |  |  |  |
| Cable Size |  |  |  |  |  |  |  | Voltage Rating |  |  |  |  |  |  |  |
| Cable Cores |  |  |  |  |  |  |  | Sheath Colour |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Location A |  |  |  | Location B |  |  |  |
| Termination Diagram |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INSULATION RESISTANCE AND CONTINUITY TEST – CORES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 |  |  | 11 |  |  |  | 21 |  | 31 |  |  |  | 41 |  |  |
| 2 |  |  | 12 |  |  |  | 22 |  | 32 |  |  |  | 42 |  |  |
| 3 |  |  | 13 |  |  |  | 23 |  | 33 |  |  |  | 43 |  |  |
| 4 |  |  | 14 |  |  |  | 24 |  | 34 |  |  |  | 44 |  |  |
| 5 |  |  | 15 |  |  |  | 25 |  | 35 |  |  |  | 45 |  |  |
| 6 |  |  | 16 |  |  |  | 26 |  | 36 |  |  |  | 46 |  |  |
| 7 |  |  | 17 |  |  |  | 27 |  | 37 |  |  |  | 47 |  |  |
| 8 |  |  | 18 |  |  |  | 28 |  | 38 |  |  |  | 48 |  |  |
| 9 |  |  | 19 |  |  |  | 29 |  | 39 |  |  |  | 49 |  |  |
| 10 |  |  | 20 |  |  |  | 30 |  | 40 |  |  |  | 50 |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Earth |  |  |
| Tester Type |  |  |  |  |  | Tester Serial No. |  |  |  | Test Volts |  |  |  |  |  |
| INSTALLATION INSPECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection |  |  |  |  |  |  |  | Location A |  |  |  | Location B |  |  |  |
| Cable Gland and Shroud Fitted Correctly |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable Number Tag Fitted and Correct |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable Core Ferrules Fitted and Correct |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable Cores Terminated Correctly |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  |  |  | Inspected By: Print Name: Sign: |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |  |  |  |

# ET 22 CONTROL CABLE INSPECTION AND TEST SHEET (Page2 of 2)

| PROJECT TITLE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cable Number |  |  |  |  |  |  |  | Cable Type |  |  |  |  |  |  |  |
| Cable Size |  |  |  |  |  |  |  | Voltage Rating |  |  |  |  |  |  |  |
| Cable Cores |  |  |  |  |  |  |  | Sheath Colour |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Location A |  |  |  | Location B |  |  |  |
| Termination Diagram |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INSULATION RESISTANCE AND CONTINUITY TEST – CORES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 |  |  | 11 |  |  |  | 21 |  | 31 |  |  |  | 41 |  |  |
| 2 |  |  | 12 |  |  |  | 22 |  | 32 |  |  |  | 42 |  |  |
| 3 |  |  | 13 |  |  |  | 23 |  | 33 |  |  |  | 43 |  |  |
| 4 |  |  | 14 |  |  |  | 24 |  | 34 |  |  |  | 44 |  |  |
| 5 |  |  | 15 |  |  |  | 25 |  | 35 |  |  |  | 45 |  |  |
| 6 |  |  | 16 |  |  |  | 26 |  | 36 |  |  |  | 46 |  |  |
| 7 |  |  | 17 |  |  |  | 27 |  | 37 |  |  |  | 47 |  |  |
| 8 |  |  | 18 |  |  |  | 28 |  | 38 |  |  |  | 48 |  |  |
| 9 |  |  | 19 |  |  |  | 29 |  | 39 |  |  |  | 49 |  |  |
| 10 |  |  | 20 |  |  |  | 30 |  | 40 |  |  |  | 50 |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Earth |  |  |
| Tester Type |  |  |  |  |  | Tester Serial No. |  |  |  | Test Volts |  |  |  |  |  |
| INSTALLATION INSPECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection |  |  |  |  |  |  |  | Location A |  |  |  | Location B |  |  |  |
| Cable Gland and Shroud Fitted Correctly |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable Number Tag Fitted and Correct |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable Core Ferrules Fitted and Correct |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable Cores Terminated Correctly |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COMMENTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inspection and Test Date: |  |  |  |  |  | Inspected By: Print Name: Sign: |  |  |  | Confirmed By: Print Name: Sign: |  |  |  |  |  |
| Anglo Supervisor Print Name: Sign: |  |  |  |  |  |  |  | EEM (or EEM delegate) Print Name: Sign: |  |  |  |  |  |  |  |

# ET 23 	SWITCHBOARD INSPECTION SHEET

The Following Should be performed for each switchboard at the location or on the piece of equipment. Faults found should be rectified at the time & a work order raised detailing items & outstanding work. Return Sheet to Electrical Supervisor when complete.

| Date :- | Plan Unit No :- |
| --- | --- |
| Switch Board No :- | Location: - |
| Inspection By :- | Work/Order :- |

| ET 23 SWITCHBOARD INSPECTION SHEET |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description |  | Y/N | Comment / Defect |
| 1 | Are Approaches to the doors satisfactory? Doors open to 90 Degrees & 600 mm Un-obstructed access into board. |  |  |  |
| 2 | Is the Switchboard Exposed to the weather or is it mounted indoors? |  |  |  |
| 3 | Switch boards front panel Colour Coded :- 0 – 600 V :- Grey, White or Orange. 600 – 1000 V :- Blue. >1000 V ( High Voltage ) :- Fire Engine Red. |  |  |  |
| 4 | Are the Following signs present on the outside panel of the switchboard. |  |  |  |
|  |  | Switch Board Identification No:- & Description. |  |  |
|  |  | Sign Showing where it is fed is from. |  |  |
|  |  | Voltage Signs Indicating circuits running through this panel. |  |  |
|  |  | “Authorised Access Only” Sign. |  |  |
| 5 | If Controls are Mounted on Outside Front Panel. Are all Correctly Labelled & Indication Lights Operational? |  |  |  |
| 6 | To Open Outside Panel, Is a dedicated Tool Required ? ( Electrical Key or Door tool ). |  |  |  |
| 7 | Is the Switchboard Securely Mounted ? |  |  |  |
| 8 | Is the outside of The switchboard clear of any damage or holes that would allow Moisture or Dust to enter? |  |  |  |
|  | If Outdoors, does it meet IPP 55 Standards with Rubber Seals etc? |  |  |  |
| 9 | Are all Door Seals in Place? |  |  |  |
| 10 | Are all hinges & Fastening points in tact. & Door Correctly Hung, Closing & Sealing properly? ( Door Handles, Panel Bolts etc.. ) |  |  |  |
| 11 | Gutters Clean & Clear of Rust & Debris? |  |  |  |
| 12 | If inside Swing Panel is Fitted ? |  |  |  |
|  |  | Are all holes sealed so Live Parts cannot be accidentally accessed? |  |  |
|  |  | Are all Circuit Breakers Labelled & Switchboard Legend available? |  |  |
|  |  | Is 30 mAmps E/L fitted to all Circuit Breakers feeding GPO & Lighting Circuits. |  |  |
|  |  | Is Earth Leakage Fitted to main Breaker. What Trip Current & Time setting? |  |  |
| 13 | To gain access to Conductors past Swing Panel |  |  |  |
|  |  | Is a dedicated Key or Tool required? |  |  |
|  |  | Is an interlocking device fitted on Main CB to ensure board is de energised before entry to conductors is gained ? |  |  |
|  |  | Is a Door Switch or Trip Device Fitted on inside panel? |  |  |
|  |  | Isolate Elsewhere signs fitted as required? |  |  |
| 14 | With panel open, are all Line Side barriers intact & effective? |  |  |  |
| 15 | Inside Condition of Panel |  |  |  |
|  |  | Any Signs of Heating? |  |  |
|  |  | Signs of Water Ingress? |  |  |
|  |  | Relatively Clean of Dirt, dust & Cob Webs? |  |  |
| 16 | Control Supplies Inside Switch Board. 110 Volt Centre tapped? ( Check that no 240 Volt control Supplies leave Enclosure, Unless 30 mAmp E/L Fitted is fitted to these ). |  |  |  |
| 17 | Are all Circuit Breakers fitted with a Lockable Isolator facility? List Those that aren’t |  |  |  |
| 18 | Are Earths fitted to all Panels of the Enclosure that have live parts mounted on them? |  |  |  |
| 19 | Do all E/L trip Devices & Emergency Stops operate correctly? Before testing, check what equipment will be tripped out & notify operators if required? |  |  |  |
| 20 | Fire Extinguishers present & Tagged in last 6 Months? |  |  |  |
| 21 | Are Electrical Drawings available in switchboard? |  |  |  |
| 22 | Are Electrical Drawings available on Site? |  |  |  |
| 23 | Do the Drawings have sufficient detail, about protection settings, E/L, Transformer sizes etc? |  |  |  |
| 24 | Lighting around Switchboard adequate for Night Work ? |  |  |  |
| 25 | Emergency Lighting present & operational? ( For review purposes only ) |  |  |  |
| 26 | LV Rescue Kit Present & within 6mths tests? ( For review purposes only ) |  |  |  |
| 27 | Are all cables into & out of board correctly marked & identified? |  |  |  |

Summary List Of Outstanding Items to be done :-

| Work Order | Description/Action Required |
| --- | --- |

PM’s & Scheduled Maintenance Currently Performed :-

| Description | Service Code | Frequency | Last Done |
| --- | --- | --- | --- |

| ET 23 SWITCHBOARD INSPECTION SHEET SIGNOFF |  |  |  |
| --- | --- | --- | --- |
| Inspection and Test Date: | Inspected By: Print Name: Sign: |  | Confirmed By: Print Name: Sign: |
| Anglo Supervisor Print Name: Sign: |  | EEM (or EEM delegate) Print Name: Sign: |  |

# DOCUMENT INDEX

SAFETY	3

1.	PURPOSE	3

2.	SCOPE	3

3.	REFERENCES	4

4.	SPECIFIC REQUIREMENTS	5

APPENDIX: STANDARD TEST SHEETS	14

ET 1	0.6/1.1 kV POWER CABLE INSPECTION AND TEST REPORT	15

ET 2	HIGH VOLTAGE CABLE INSPECTION AND TEST REPORT	16

ET 3	EARTH GRID INSPECTION & TEST REPORT	17

ET 4	TRANSFORMER INSPECTION AND TEST REPORT (Page1 of 2)	18

ET 4	TRANSFORMER INSPECTION AND TEST REPORT (Page2 of 2)	19

ET 5	 SWITCHGEAR INSPECTION AND TEST REPORT	20

ET 6	DISTRIBUTION EQUIPMENT FUNCTION CHECK LIST	22

ET 7	 TRANSFORMER OIL TEST REPORT	24

ET 8	CONVEYOR ELECTRICAL COMMISSIONING INSPECTION AND TEST REPORT	25

ET 9	OVERCURRENT AND EARTH FAULT PROTECTION RELAYS	27

ET 10 	AC MOTOR COMMISSSIONING TEST REPORT	29

ET 11 SMALL MOTOR & ELECTRICAL EQUIPMENT COMMISIONING TEST REPORT	31

ET 12 	MOTOR CONTROL CENTRE CUBICLE ELECTRICAL   INSPECTION AND TEST REPORT	32

ET 13	 MISCELLANEOUS ELECTRICAL TEST REPORT	34

ET 14	MISCELLANEOUS DRIVE COMMISSIONING TEST REPORT	35

ET 15 MOTOR CIRCUIT & ROTOR CABLE TEST SHEET (Page1 of 2)	37

ET 15 MOTOR CIRCUIT & ROTOR CABLE TEST SHEET(Page2 of 2)	38

ET 16 LIGHTING CIRCUIT INSPECTION AND TEST SHEET (Page1 of 2)	39

ET 16 LIGHTING CIRCUIT INSPECTION AND TEST SHEET (Page2 of 2)	40

ET 17	 GPO CIRCUIT TEST SHEET (Page1 of 2)	41

ET 17	 GPO CIRCUIT TEST SHEET (Page2 of 2)	42

ET 18	WELDING OUTLET CIRCUIT TEST SHEET (Page1 of 2)	43

ET 18 WELDING OUTLET CIRCUIT TEST SHEET (Page2 of 2)	44

ET 19  	HIGH VOLTAGE POWERLINES AND SWITCHYARDS INSPECTION SHEET	45

ET 20	HIGH VOLTAGE AERIALS AND SWITCHYARD TEST SHEET	46

ET 21	 BATTERY CHARGER TEST SHEET (Page1 of 2)	47

ET 21	  BATTERY TEST SHEET (Page2 of 2)	48

ET 22 CONTROL CABLE INSPECTION AND TEST SHEET (Page1 of 2)	49

ET 22 CONTROL CABLE INSPECTION AND TEST SHEET (Page2 of 2)	50

ET 23 	SWITCHBOARD INSPECTION SHEET	51

DOCUMENT INDEX	55